{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Check Sheet（防灾）"],"not_rendered":{"charts":0,"images":6,"macros":0,"external_links":2,"defined_names":33,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Check Sheet（防灾）","index":0,"n_rows":33,"n_cols":39,"rows_kept":33,"cut":false,"hidden":false,"merged":[[22,2,22,13],[22,14,22,20],[23,2,23,3],[23,5,23,8],[23,9,23,12],[23,15,23,18],[23,19,23,20],[29,2,29,19],[28,2,28,3],[28,6,28,20],[24,5,24,8],[24,9,24,12],[27,5,27,8],[27,9,27,12],[27,19,27,20],[24,19,24,20],[26,5,26,8],[24,15,24,18],[26,15,26,18],[27,15,27,18],[26,19,26,20],[25,5,25,8],[26,9,26,12],[12,18,12,20],[11,2,11,4],[11,5,11,8],[11,9,11,11],[11,12,11,14],[11,15,11,17],[12,2,12,4],[12,5,12,8],[12,9,12,11],[12,12,12,14],[12,15,12,17],[25,15,25,18],[25,19,25,20],[15,2,17,20],[28,4,28,5],[2,1,2,21],[7,2,7,4],[7,5,7,11],[7,12,7,17],[7,18,7,20],[8,2,8,4],[8,5,8,11],[8,12,8,17],[8,18,8,20],[10,2,10,11],[10,12,10,20],[11,18,11,20]]}
[]
[]
[null,"电池栋OHT增设 稼动前防灾点检"]
[]
[]
[null,null,"1. 점검개요 点检概要"]
[]
[null,null,"구   분\n区分",null,null,"설비명\n设备名",{"$nulls":6},"제조사\n制造商",{"$nulls":5},"嫁动预计日"]
[null,null,"내   용\n内容",null,null,"电池栋OHT增设 稼动前防灾点检",{"$nulls":12},"不允许稼动"]
[]
[null,null,"검수자\n验收者",{"$nulls":9},"주요 점검내역\n主要点检内容"]
[null,null,"安全环境G",null,null,"组立技术2G",null,null,null,"제조사\n制造商",null,null,"점검일\n点检日期",null,null,"관리번호\n管理no",null,null,"검토결과\n检讨结果"]
[null,null,"张靖东",null,null,"金靖",{"$nulls":6},"2021.8.11",null,null,"韩立伟",null,null,"不允许稼动"]
[]
[null,null,"2. 점검결과 요약 点检结果概要"]
[null,null,"①建筑主体火灾自动报警系统（火灾报警探测器、空气采样管）被OHT底部隔板遮挡，如发生紧急情况时，无法迅速感知报警\n②建筑主体自动喷水灭火系统（消防喷淋）被OHT底部隔板遮挡，如发生紧急情况时，无法迅速进行喷水灭火\n③设备增设前未进行-事前影响评价\n④设备增设前未进行LAYOUT变更申请"]
[]
[{"$nulls":38},"                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                          "]
[]
[]
[]
[null,null,"3. 주요 문제점 및 개선항목 요구표 主要问题点及改善项目要求"]
[null,null,"개선항목 요구표  改善项目要求",{"$nulls":11},"실행계획 완료표 执行计划完了表"]
[null,null,"점검대상\n点检对象",null,"일련\n번호\n履历号码","점검결과\n点检结果",null,null,null,"사진\n照片",null,null,null,"납기\n요청\n纳期邀请","완료\n完了","조치후 사진\n改善后照片",null,null,null,"等级"]
[{"$nulls":4},1,"建筑主体自动报警系统（火灾报警探测器、空气采样管）被OHT底部隔板遮挡，如发生紧急情况时，无法迅速感知报警",{"$nulls":9},"건물 본체 자동 경보 시스템(화재 경보 감지기, 공기 샘플링 튜브)은 OHT 하단 파티션에 의해 가려지며, 비상 사태가 발생하면 경보를 신속하게 감지할 수 없습니다",null,null,null,"A"]
[{"$nulls":4},2,"建筑主体自动灭火系统（消防喷淋）被OHT底部隔板遮挡，如发生紧急情况时，无法迅速进行动作灭火",{"$nulls":9},"건물 본체 자동소화시스템(소방스프링클러)은 OHT 하단 칸막이에 가려져 있어 유사시 신속한 동작 소화가 불가능합니다",null,null,null,"A"]
[{"$nulls":4},3,"设备增设前未进行-事前影响评价",{"$nulls":9},"장비 증설 전 -사전 영향 평가 실시안",null,null,null,"A"]
[{"$nulls":4},4,"设备增设前未进行LAYOUT变更申请",{"$nulls":9},"장비 증설 전에 LAYOUT 변경 신청이 진행되지 않았습니다",null,null,null,"A"]
[{"$nulls":4},"검수\n현황\n验收现况",null,"问题点改善后，再次确认!                                                                                "]
[]
[]
[null,null," "]
[null,null,null,"   ",{"$nulls":9}," "]